## BoQ Summary
NAIVASHA AOD PROJECT
BILLS OF QUANTITIES
SUMMARY OF BILLS OF QUANTITIES
Bill No. | Description | Amount (Kshs)
1 | PRELIMINARIES & GENERAL
2 | MARARO TANK
3 | CONSUMER METERS
4 | MARARO DISTRIBUTION NETWORK
5 | KAYOLE MARARO RISING MAIN
6 | MIRERA DISTRIBUTION NETWORK
7 | KINAMBA DISTRIBUTION NETWORK
8 | KEROCHE BLOCK SYSTEM
BILL TOTAL
Contingencies (5%)
Bills Total inclusive of Contingencies
Value Added Tax (16%)
TOTAL CARRIED TO FORM OF BID

## ESMP
ESMP Cost
Item | Description | Amount (Kshs) | Remarks
1 | ESMP Costs
1.1 | Management Actions for : Lack of proper access and alternative routes.
| Develop a traffic management plan and seek its approval by the Police Traffic Department | 300000 | (Cost of traffic signages = 60,000, hiring traffic police and traffic marshalls (4,000 per day for 60 days = 240,000) 60 days estimated time for construction that may need traffic managemnt
Installation of appropriate signages to direct and control human and vehicular traffic
Provision of Temporary alternative routes of access during trenching and pipelaying across any road
Prior information to project affected communities before disruptive works commence
Deploy trained traffic marshals during works to direct all kinds of traffic
Seek approval of Police Traffic Department of the traffic management plan prior to construction including approval of obstruction times during construction.
The proponent should apply for way-leaves from relevant Authorities (KENHA, KURA & KeRRA) and the County governments to secure approvals in good time
Road crossing related activities to be hastened so as to take minimal time possible
Right classes water pipes to be used at the sections of road crossings so as to avoid frequent bursts and damages to the pipe
1.2 | Management Actions for : Broken water/ sewer pipes & Communication cables.
| Identify and mark the location of existing underground services | 200000 | (payment to 10 personel locating and marking the trial pits: 2000 per day for 5 days=100,000; fuel for movement to different locations for marking =10,000, repairing accidentally damaged utility lines=90,000)
Excavating manual trial pits to locate the underground infrastructure facilities before using mechanical excavation
Consult utility service providers before any utility is affected
Issue notices to the potentially affected persons before any service disruption, stating clearly the duration over which services will be interrupted
1.3 | Management Actions for : Potential of increased respiratory infections, eye irritations and allergic reaction amongst affected people
| Long haul routes with not more than 10 km will be avoided when considering diversions. Clearance lots to be approved by Project Manager. | 50000 | (hiring 10,000 litre wter bowser for sprinkling: 20 litres at 20/= =10,000 plus fuel for the whole project period- 20,000) PPEs (nose masks) for workers for the project periods (60 days-approximately 20,000)
Where dust is identified as an issue, dust control measures such as water sprinkling will be implemented. ,
Contractor to prepare a Traffic Management Plan that spells speed limits at construction areas and near sensitive receptors.
Conduct air quality management awareness amongst workers
Avoid excavation works in extremely dry weather consitions
Personal Protective equipment to be worn by workers PPEs to include dust masks and / or suitable aspirators
Manage excavated soil by covering those that are not of immediate use
Restrict excavations to the project foot-print to minimize surfaces exposed to wind erosion
The contractor should inform the management of sensitive institutions on the days that excess dust is likely to be generated so they can be prepared.
1.4 | Management Actions for : Potential Noise and vibration nuisance to the residential units and institutions around the project site.
| Pre-start checks and maintenance schedules to ensure equipment performance is as required; | 80000 | (procuring of of ear muffs/ plugs for the entire period-60 days- lumpsum amount of 30,000; Designing and mounting posters/ signages=50,000)
Noise-dampening equipment to be used on equipment with excessive noise generating characteristics;
All construction workers at the site and the yard shall comply with the worker’s code of conduct which include compulsory wearing of PPEs
Drivers to be instructed to avoid unnecessary hooting in near schools and hospitals
Construction activities to be restricted to day time operations from 8am - 5pm
Issue early warning notices of impending heavy steel works to allow for better preparation of the potentially affected
Preorder steel structures from manufacturers that will require very minimal works at the site to reduce noise related to grinding and welding
Sensitize construction workers on need to avoid excessive noise and vibration.
1.5 | Management Actions for : Cutting of trees, shrubs and clearing of bushes to pave way for works.
| Provide site specific information to the workers on vegetation that should not be cut | 70000 | (sourcing and planting trees in appropriate areas along the 114km pipeline coverage: 1 seedling at 20 shillings x 350 seedlings) 10 times
Include toolbox talks for site specific vegetation information
Ensure proper demarcation of the project area to be affected by construction works.
The use of fuel wood by construction workers should be discouraged. Workers should be encouraged to use clean energy sources.
The contractors to ensure suppliers are legally compliant and environmentally sensitive.
Ensure traffic is restricted to established diversions and speed limits observed.
Apply for tree cutting permits whenever necessary in line with the law.
Ensure that for every tree that will be cut down at least 10 trees seedlings to be planted
1.6 | Management Actions for : Spillage of hydrocarbon into soil thus affecting soil micro and macro nutrients.
| Proper regular servicing and maintenance of machines that will be used at the site | 150000 | (soil remediation-soil sample collection and analysis-50,000 remediation process=100,000
All vehicles and machines should be serviced at designated service bays
In case of oil spillage, remedial action should be taken that includes scooping of the contaminated soil and disposing at a licensed waste site.
1.7 | Management Actions for : Erosion Siltation of storm water drains Flooding
| Project activities to be carried out only on the project demarcated areas | 120000 | Soil sediment traps=100,000, reeping off compacted surfaces=20000,
Backfilling to be done as soon as possible to avoid loose soil being eroded
Vehicle movements should be restricted to the defined roads/tracks paths.
Grassing of the disturbed areas to be done upon completion of works at the specific site
1.8 | Management Actions for : Loss of aesthetics and potential pollution leading to disease outbreak.
| Provide appropriate segregated waste bins, type, and volume and service frequency to accommodate anticipated waste streams at the contractor’s camp | 310000 | (potable toilets: assuming works will be carried out at three different sites, 2x3=6 toilets. Each toilet=20000x6=120,000 plus 2 -for females and males at the camp site=40,000) total=160,000 Cost of liquid waste collection and disposal=10,000 every week for 15 weeks (60 days) =150,000 Grand total= 310000
Provide portable toilets to workers at all working points
Keep toilets in hygienic conditions
Provide information regarding waste management in site specific inductions, including waste separation and importance of securing vehicle loads.
Tool box talk on solid waste management
Recycle most of the recyclable wastes.
Through accurate estimation of the sizes and quantities of materials required, order materials in the sizes and quantities they will be needed, rather than cutting them to size, or having large quantities of residual materials.
Donate recyclable/reusable or residual materials
Engage a licensed solid waste handler to collect and dispose of the wastes
1.9 | Management Actions for : Increased number of new infection and increased disease burden in the community
| Regular voluntary testing of project staff and counseling for the infected persons in the project team | 360000 | (procuring protection devices per week for an approximate male population of 100, each device costing 80/=. Total =8000x15 weeks x3 protection devices per day
Availing of educational materials at strategic point within the project area
Provision of protective measures against spread of HIV such as condoms both for females and males to the workers
2 | Management Actions for : Demonstration due too unclear recruitment process
| Contractor to ensure there is labour management plan | 50000 | (Allowances for labour committee sittings@5000 per sessions for 10 sessions
Contractor to work closely with community liaison officer in the process of recruitment
Locals be given priority when sourcing for labour force
Labour laws to be strictly adhered to in terms of minimum wages, recruitment process, overtime payments among other
2.10' | Management Actions for : Wastes generated during camp construction and operations may pollute the environment (both liquid and solid wastes)
| Provision of toilets | 480000 | Hiring a NEMA license waste handler for th e project period @ 40,000.00 per month for 12 months implementation period
Monitor leakage to the environment
The toiletsto be kept cleac always
Site waste collection point to be placed more than 20m awy from water bodies/ sources
Communities shall be involved in the identification of campsite to avoid conflict
Placement of spoil is to be done in such a manner to minimize the spread of materials and the impact on surrounding vegetation and that no materials ‘creep’ into ‘no-go ’areas.
Construction wastes (residual earth, debris and scrap materials) to be removed for safe disposal.
Encourage recycling where possible (concrete debris for access road surfacing),
Provide labeled litter bins
Contract NEMA approved wast collector
Contaminated organic matter in the work areas to be isolated for safe disposal.
2.11' | Management Actions for : Accidental falls from heights during steel water tank installation, Risk of cuts from the shape steel, Risk of accidental pricks from metals
| For those working at heights, provide height safety fasteners. | 300000 | Purchase of PPEs and their replacement for an approximated workforce of 100 laboureres Kshs 3,000.00
All workers should always be adorned in the relevant personal safety equipment
The contractor should acquire necessary permits for working at heights
Workers training and sensitization should be implemented
All workers should have personal work insurance in case of any accidents for easier payment of claims
Availing fully stocked first aid kits for any emergencies while working at the site
2.12' | Management Actions for : Potential Noise and vibration nuisance to the residential units
| Issue early warning notices of impending heavy steel works to allow for better preparation of the potentially affected | 240000 | Periodic Noise Survey @ Kshs.60,000.00 for 4 quarters
Preorder steel structures from manufacturers that will require very minimal works at the site to reduce noise related to grinding and welding
Sensitize construction workers on need to avoid excessive noise and vibration.
Ensure that all construction equipment is serviced and are in good condition
Limit all construction activities to daytime hours and in strict adherence to NEMA permits
Provision of relevant PPEs for the active sites with potential for noise and vibration ( Ear muffs)
2.13' | Management Actions for : Disputes arising from the project stakeholders (beneficiary settlements dwellers, Private WSPs, Business community, regulatory Agencies)
| Strong and functional GRC be put in place. | 200000 | Refreshments for the GRC meetings 20 meetings @ Kshs. 10,000.00 per meting)
Strong Stakeholder Engagemnet Plan (SEP) be put in place during construction phase
Facilitate liaison officers to handle a wide range of grievances in their respective areas
Contractor to employ a residence Safeguards team
Strengthen the capacity of GRC to handle such tools as stakeholder register, grievance form, commitment register and grievance log form
Relevant MoU’s to be developed to guide relavant engagements including intregration and collapboration with key stakeholders
Sub Total ESMP AMOUNT |  | 2910000
| Sub Total Carried to Item A1008: Bill No. 1 P&G | 2910000

## Bill No. 1 P&G
PRELIMINARIES AND GENERAL
ITEM | DESCRIPTION | UNIT | QUANTITY | Rate | Amount
CLASS A: GENERAL ITEMS
Setting out and Survey
A1001 | Allow for Establishment of Level Datum and Setting Out of the Works in all the Project Areas in accordance with the Specifications. This shalll include staking out of the Pipeline Routes. Include for preparation and submission of Setting Out Survey Report to the Engineer for approval. | Item | L.S
Signboards
| Allow for Provision, erection and maintainance of Project Sign Boards at sites to be indicated by the Engineer within the Project Area and removal upon completion of the Contract. Details of the Sign Board are shown on Drawing. | Nr | 4
Other Provisional Sums
A003 | Allow a Provisional sum for the Engineer's miscellaneous, project design and project supervision account to be spent in whole or part as instructed by the Engineer | sum | 1 | 3000000 | 3000000
A1004 | Specific Conditions
A1005 | Allow for all specific works related to working along active pipelines and maintaining continuity of water supply and sewer operation including protection of supports etc. of existing pipelines during constructionactivity. | sum | 1
A1006 | Allow for preparation of as-build drawings and project completion reporting. | sum | 1
A1007 | Contractors overhead and profit items 1A003 | % | 10
A1008 | Provision for Compliance to Project ESMP as specified | L.S | 1
A1009 | Allow for provisional sum of kes 500,000 for provision of safety and personnal protective equipment for Project Engineer and Project Engineer's staff and client's representative while on site for the duration of the project | Item | 1 | 500000 | 500000
A1010 | Allow for a provisional sum of kes 300,000 for environmental management and traffic management (incl notifications and works signs) for the duration of the project | Item | 1 | 300000 | 300000
PAGE TOTAL CARRIED FORWARD TO BILL COLLECTION SHEET

## Bill No. 2 MARARO TANK
BILL No. 2-MARARO TANK
ITEM No. | DESCRIPTION | UNIT | QUANTITY | RATE | AMOUNT
CLASS A: GENERAL ITEM
Specified Requirements
Testing of Works
A2001 | Allow for water tightness tank for the satisfaction of the Engineer | l.s | 1
A2002 | Disinfection of Tanks: flushing with clear water, filling with water containing 0.05g/l calcium hyperchlorite, left for 24 hours. This includessupply of necessary equipment, materials, chemicals and water, measurement of residual chlorine, all as specified and safe disposal of disinfecting water to Engineer's approval. | l.s | 1
A2003 | Allow for keeping trenches and other excavation free of water which may have entered through ground seepage, rain or by other means as directed by the Engineer. | l.s | 1
A2004 | General clearance with the tank costruction area, width n.e 1.5m | ha | 0.2
Cutting of trees
A2005 | Girth 0.5m - 1.0m | nr | 3
A2006 | Girth 1.0m - 2.0m | nr | 2
TANKS
A2007 | Supply and Install Complete 250m3 Silo Tank including foundation and mobilization to site | nr | 1
A2008 | DN160 Flange adaptor | nr | 1
A2009 | DN 160 double flanged 90 degree bend | nr | 1
A2010 | 160mm double flanged steel pipe 3000mm long | nr | 1
A2011 | 160mm double flanged pipe 1000mm long with puddle flange | nr | 1
A2012 | 160 flanged float Valve | nr | 1
A2013 | 160mm dia Stepped coupling | nr | 1
A2014 | All flange 160mm sluice valve | nr | 1
A2015 | All flange 200mm sluice valve | nr | 1
A2016 | 200mm dia Stepped coupling | nr | 1
A2017 | Valve Chambers | nr | 2
A2018 | Allow for sum for fencing works, lighting complete with a gate within the tank area | nr | 1
Operator store within the Mararo tank area
General excavation
A2019 | Top soil maximum depth 0.25- 0.5 | m³ | 11.56
Excavate in material other than topsoil, rock or artificial hard material
A2020 | Maximum depth 0.5- 1m | m3 | 3.17
A2021 | In material class" A" | m3 | 1
Excavation ancillaries
A2022 | Trimming of excavated surface | m² | 5.28
A2023 | Preparation of excavated surface | m² | 11.6
A2024 | Preparation of excavated surface | m² | 11.6
Disposal of excavated material
A2025 | Disposal of excavated material other than topsoil, rock or artificial hard material | m3 | 3.17
A2026 | Disposal of excavated rock | m3 | 1
IN SITU CONCRETE
Placing of concrete
A2027 | Mass concrete blinding thickness not exceeding 150mm | m3 | 1.1
Reinforced Concrete class 25/30
A2028 | Bases, Footings, Ground Slabs, Walls and Beams or Columns | m3 | 2.05
CONCRETE ANCILLARIES
Formwork fair finish
Plane vertical to:
A2029 | Width :0.1-0.4 m | m2 | 17.51
Reinforcement
Deformed high yield steel
A2030 | Nominal diameter 6-20mm | Ton | 0.16
Brickwork, blockwork and masonry
A2031 | 300mm thick Solid burnt clay brickwork to BS 3921, jointed with ordinary 1:4 cement mortar, hoop irons every three courses | m² | 21
A2032 | 300mm thick Damp proof course of bitumen impregnated fabric to BS 6398 | m | 10
Painting
A2033 | Oil paint in three coats on external masonry walls inclined at an angle exceeding 60 degrees to the horizontal | m² | 41.64
A2034 | Oil paint in three coats on 'Upper surfaces of facial board inclined at an angle not exceeding 30 degrees to the horizontal | m² | 41.64
A2035 | Emulsion paint in three coats on 'Upper surfaces of facial board inclined at an angle exceeding 60 degrees to the horizontal | m² | 41.6
A2036 | Emulsion paint in three coats on internal masonry wall inclined at an angle not exceeding 30 degrees to the horizontal | m² | 35.6
Waterproofing
Roofing
A2037 | Waterproof sheeting upper surfaces inclined at an angle not exceeding 300 to the horizontal;6mm Bituminous felt | m² | 19.46
Protective Layers
A2038 | Sand cement screed of 1:3 cement sand mortar, applied to concrete, 25 mm thick, prepared and applied to surfaces of floors inclined at an angle not exceeding 30 degrees to the horizontal | m² | 3.24
SIMPLE BUILDING WORKS INCIDENTAL TO CIVIL ENGINEERING WORKS
Doors
A2039 | Supply and installation of exterior doors with one or two steel doors, accompanied by at least three hinges, with mortise lock strike plate with rim and accompanied by at least three hinges, with mortise lock strike plate with rim and chrome, including the supply and installation of marble threshold Single leaf louvered door with size 900 mm x 2100 mm high filled in with 100 x 2mm thick mild steel louvers welded to frame. | nr | 1
Windows
A2040 | Supply and installation of windows with crystals, performed with frames made by steel with open joints, mm of section 45 (for fixed frames) and 52 mm (for opening swinging doors ), complete with sills 45 mm with lateral development of the flaps - 2 cm, internal thickness 12/10 of internal flaps, interior and exterior trims - for covering the cables - safety crystals 3 +3, or ventilation grid - fixed aluminum type - hinges and locking devices of movement against the birds, which comprises the production of the lintel reinforcing iron and the formworks, all anchored to the walls of buildings and shoulders, to be carried in reinforced concrete, including the respective reinforcing iron and the formworks, all anchored to the walls of buildings 400 x 600mm high comprising 200mm pvo complete with 4mm thick clear glass panes and burglar proofing | nr | 2
PAGE TOTAL CARRIED FORWARD TO BILL COLLECTION SHEET

## Bill No.3 - CONSUMER METERS
BILL No. 3-CONSUMER WATER METERS
ITEM No. | DESCRIPTION | Unit | Quantity | Amount
A3001 | Procure, supply and install DN 15 (1/2") DIEHL cold water meters, R160 or equivalent. | Nr | 3000
A3002 | Saddle clamp 25mm x 3/4" | Nr | 1200
A3003 | Saddle Clamp 32mm x 3/4" | Nr | 1500
A3004 | Saddle Clamp 40mm x 3/4" | Nr | 300
A3005 | Hex Nipple 3/4" | Nr | 3000
A3006 | 3/4" Peglar Gate Valve | Nr | 3000
A3007 | 25mm x 3/4" PPR Male Adaptor | Nr | 3000
A3008 | 25mm PPR Pipe | Nr | 3000
A3009 | 25mm PPR Plain Elbow | Nr | 6000
A3010 | 25mm x 1/2" PPR Male Elbow | Nr | 6000
A3011 | 1/2" Gate Valve | Nr | 3000
A3012 | 1/2" G.I Union | Nr | 3000
PAGE TOTAL CARRIED TO BILL COLLECTION PAGE

## Bill No. 4-MARARO -KAYOLE DIST
BILL No. 4-MARARO DISTRIBUTION
ITEM No. | DESCRIPTION | Unit | Qunatity | Rate | Amount
CLASS A: GENERAL ITEM
Specified Requirements
Testing of Works
A4001 | Allow for hydrostatic pressure testing as specified for all the pipelines constructed under the contract to the satisfaction of the Engineer. | m | 25868
A4002 | Disinection of Pipelines: flushing with clear water, filling with water containing 0.05g/l calcium hyperchlorite, left for 24 hours. This includes supply of necessary equipment, materials, chemicals and water, measurement of residual chlorine, all as specified and safe disposal of disinfecting water to Engineer's approval. | m | 25868
Traffic Control and General Clearance
A4003 | Allow for temporary works for diversion of traffic during construction of pipelines across roads, including sign posting, liaison with Traffic Police Department, Local Authority construction of diversion roads etc. all to the satisfaction of the Engineer. Include provision for maintaining temporary vehicular access to individual plots at all times. | L.S | 1
A4004 | Allow for keeping trenches and other excavation free of water which may have entered through ground seepage, rain or by other means as directed by the Engineer. | L.S | 1
A4005 | General clearance along the pipeline parth, width n.e 1.5m | ha | 3.8802
Cutting Trees
A4006 | Girth 0.5m - 1.0m | Nr | 9
A4007 | Girth 1.0m - 2.0m | Nr | 4
CLASS B: PIPEWORK - PIPES
Supply, transport to site and store Note: The following have been used to specify pipe diameters/types/classes. Pipe dimensions/working pressuresshall conform to KS150 -1452 - Part 2:2009.
High Density Polyethylene Pipes HDPE 100 SDR 17, ISO 4427:2007 with Butt Fusion (seamless) Jointing
B4001 | DN 200mm PN10 | m | 2578
B4002 | DN 110mm PN10 | m | 1580
B4003 | DN 90mm PN 10 | m | 2756
B4004 | DN 75mm PN 10 | m | 1700
B4005 | DN 63mm PN 10 | m | 761
B4006 | DN 50mm PN 10 | m | 1434
B4007 | DN 40mm PN 10 | m | 5668
B4008 | DN 32mm PN 10 | m | 9250
B4009 | DN 25mm PN 10 | m | 141
Note: The following have been used to specify pipe diameters/types/classes. Pipe dimensions/working pressures shall conform to KS-06-149 Part 2:2000.
Transport from Site Store, Lay and Joint Pipes in Trench, include for Excavation, Preparation of Surfaces, Disposal of Excavated Material, Shoring Sides of Excavation Trenches, Backfilling and Final Reinstatement
B4009 | DN 32 - 200mm in trenches depth 1.5m - 2.0m | m | 16814.2
B4010 | Ditto but depth 2.0 - 2.5m | m | 6467
B4011 | Ditto but depth 2.5 - 3.0m | m | 2586.8
CLASS C: PIPEWORK - FITTINGS AND VALVES Rate to Include supply and installation, complete with all installation sundries such as gaskets, bolts, nut thread tapes etc and all anchoring works
OFFTAKES
A. Tank Offtakes
C4001 | 6'' x 150mm fabricated steel flanged adaptor - VJ Type, PN 16 | Nr | 0
C4001b | 8" x 150mm fabricated steel flanged adaptor - VJ Type, PN 16 | Nr | 1
C4002 | 4'' x 2.5'' Double flanged fabricated reducer | Nr | 0
C4003 | 6'' AVK Sluice Valve or equivalent. | Nr | 1
C4003b | DN 200mm AVK Sluice Valve or equivalent. | Nr | 1
C4004 | Ditto but 3'' | Nr | 2
C4005 | Double flanged 6'' GI pipe, 0.5m long | Nr | 1
C4005b | Double flanged 8'' GI pipe, 0.5m long | Nr | 1
Fittings
C4001 | 180mm x 110mm HDPE Tee, PN 10.5 | Nr | 2
C4002 | Ditto but for 180mmx 90mm | Nr | 1
C4003 | Ditto but for 180mm x 50mm | Nr | 1
C4004 | Ditto but for 180mm x 32mm | Nr | 1
C4005 | Ditto but for 110mm x 40mm | Nr | 3
C4006 | Ditto but for 75mm x 75mm | Nr | 1
C4007 | Ditto but for 75mm x 32mm | Nr | 12
C4008 | Ditto but for 63mm x 32mm | Nr | 4
C4009 | 40mm x 40mm x 40mm Y-Tee | Nr | 1
C4010 | 75mm HDPE elbow 90 Deg | Nr | 1
C4011 | 40mm HDPE elbow 90 Deg | Nr | 1
C4012 | 32mm HDPE elbow 90 | Nr | 1
C4013 | 32mm HDPE Compressed end Caps, PN 10.5 | Nr | 31
C4014 | 25mm HDPE Compressed end Caps, PN 10.5 | Nr | 1
C4015 | 1'' Peglar Gate Valve | Nr | 21
AIR VALVES & BULK METERS
C4016 | 3'' combination air release valve, PN 16, threaded ARI Type | Nr | 1
C4017 | 110mm x 3'' HDPE Saddle Clamp, PN 16 | Nr | 1
C4018 | 3'' Hex Nipple | Nr | 1
C4019 | 3'' peglar gate valve. | Nr | 1
C4020 | DN 160'' Woltman Bulk water meter, R 160 | Nr | 1
Washouts
C4021 | 160x110x160mm Fabricated Red. Steel tee | Nr | 1
C4022 | Ditto but 110X90x110mm | Nr | 1
C4023 | 6'' x 160mm fabricated steel flanged adaptor - VJ Type, PN 16 | Nr | 2
C4024 | Ditto but 4'' x 110mm | Nr | 2
C4025 | 6'' AVK Sluice Valve | Nr | 2
C4026 | Ditto but 4'' | Nr | 3
C4027 | Ditto but 3'' | Nr | 1
C4028 | 90mm butt fused stubb end complete with flanges | Nr | 1
C4029 | 110mm UPVC loose flange | Nr | 1
Chambers, ducts, culverts, crossings, thrust, anchor blocks, reinstatement and others pipework ancillaries
Valve Chambers- Internal Dimensions to fit as detailed on Drawings
Note:- Items for Work in this class shall include:- i. Excavation, preparation of surfaces, disposal of surplus excavated material, shoring sides of excavation, backfilling and removal of redundant services. ii. Concrete, Reinforcement, Formwork, Joints and Finishes. iii. Include for supply and fixing of removable precast concrete cover slab, mild steel frame, lifting / opening mechanism, step irons, compacted granular fill, rendering of exposed blockwork etc;. iv.Tips for disposal of excavated material or debris to be identified by the Contractor in liaison with the Local Authorities.
Air valve Chamber (1.5m x 1.2m)
C4030 | Depth n.e 1.5 m | Nr | 1
C4031 | Wash Out Chambers (2m x 2.4m) | Nr | 2
C4032 | Off Take Chambers (2m x 2.4m) | Nr | 2
Crossings
C4033 | Allow for crossing existing drains and sewers, and reinstate these after construction of the water line has been completed. Pipe bore 100mm-300mm | Nr | 8
Micro-tunneling below bituminous roads
Rates quoted shall be deemed to include for costs incurred on relevant roads authorities levies, traffic control, signage and safety measures during execution of the works and provision and installation of appropriate black pipe sleaves.
C4034 | DN 160 mm | m | 60
C4035 | Extra over microtunnelling in rock | m3 | 28
Reinstament
Breaking up, temporary and permanent reinstatement of murram road (Width of road cutting n.e 2m) with 300mm thick well graded stabilised gravel with 3% cement content base compacted using a 8-10 tonne roller to the satisfaction of the Engineer . Nominal bore n.e. 300mm. Contractor to allow for liason with relevant local authorities and obtaining approval for completed works in his rates. Rate quoted shall be deemed to include UPVC waste water pipes class 41 for sleave works.
C4036 | OD 32 - 75mm HDPE Pipe | m | 120
Other Pipework Ancillaries Supply and erect precast concrete marker post for the following
C4037 | Pipeline marker post | Nr | 45
C4038 | Air valve marker post | Nr | 1
CLASS D: PIPEWORK - SUPPORTS AND PROTECTION, ANCILLARIES TO LAYING AND EXCAVATION
Extra to excavation and backfilling
D4001 | Extra Over excavation items for excavation in Soft rock | m3 | 13
D4002 | -Ditto- but in Hard rock | m3 | 14
Concrete thrust blocks
Thrust blocks - RC, Volume 0.5 - 1.0m3
D4003 | For All junctions and branches | Nr | 38
PAGE TOTAL CARRIED TO BILL COLLECTION PAGE
Note on F20: Evans Rwenji: Arithmetic Error correct rate should be 470,000
Note on F177: Evans Rwenji: Error in the original calculation, the total amount was provided as 45,000 the correct value should be 232,500

## Bill No.5-KAYOLE-MARARO R.MAIN
BILL No. 5 - KAYOLE-MARARO RISING MAIN
ITEM No. | DESCRIPTION | Unit | Quantity | Rate | Amount
CLASS A: GENERAL ITEM
Specified Requirements
Testing of Works
A5001 | Allow for hydrostatic pressure testing as specified for all the pipelines constructed under the contract to the satisfaction of the Engineer. | m | 3715
A5002 | Disinfection of Pipeline ; Flushing with clear water, filling with water containing 0.05g/l Calcium Hypochlorite, left for 24 hours. This includes supply of necessary Equipment, Materials, Chemicals and Water, Measurement of Residual Chlorine, all as specified and safe disposal of disinfecting water to Engineer's approval. | m | 3715
Trafic Control and General Clearance
A5003 | Allow for temporary works for diversion of traffic during construction of pipelines across roads, including sign posting, liaison with Traffic Police Department, Local Authority construction of diversion roads etc. all to the satisfaction of the Engineer. Include provision for maintaining temporary vehicular access to individual plots at all times. | L.S | 1
A5004 | Allow for keeping trenches and other excavation free of water which may have entered through ground seepage, rain or by other means as directed by the Engineer. | L.S | 1
A5005 | General clearance along the pipeline parth, width n.e 1.5m | ha | 0.6
Cutting of Trees
A5006 | Girth 0.5m - 1.0m | Nr | 8
A5007 | Girth: 1.0 m - 2 m | Nr | 2
CLASS B: PIPE WORK - PIPES
Supply, transport to site and store Note: The following have been used to specify pipe diameters/types/classes. Pipe dimensions/working pressures shall conform to KS150 -1452 - Part 2:2009.
High Density Polyethylene Pipes HDPE 100 SDR 17, ISO 4427:2007 with Butt Fusion (seamless) Jointing
B5001 | DN 160mm PN16 | m | 0
Double flanged epoxy steel pipe
B5002 | Handle, transport and lay 200 mm double flanged steel pipe, PN 12.5 | m | 0
B5003 | Ditto but 160mm | m | 2
Transport from Site Store, Lay and Joint Pipes in Trench, Include for Excavation, Preparation of Surfaces, Disposal of Excavated Material, Shoring Sides of Excavation trenches, Backfilling and final Reinstatement.
B5004 | DN 160 - 200mm in trenches depth 1.5m - 2.0m | m | 2786
B5005 | Ditto but depth 2.0 - 2.5m | m | 743
B5006 | Ditto but depth 2.5 - 3.0m | m | 186
CLASS C: PIPEWORK - FITTINGS AND VALVES Rate to Include supply and installation, complete with all installation sundries such as gaskets, bolts, nut thread tapes etc and all anchoring works
OFF-TAKES
C5001 | 6'' x 160 fabricated steel flanged adaptor - VJ Type, PN 16 | Nr | 4
C5002 | 6'' x 6'' x 6'' flanged fabricated steel Tee | Nr | 1
C5003 | 160mm HDPE butt fused stab end complete with flange | Nr | 2
C5004 | 160MM UPVC 45 Deg Long radius bend, One side expanded PN 16 | Nr | 3
C5005 | 6'' Non Return Valve, flap type | Nr | 2
AIR VALVES & BULK METERS
C5006 | 3'' combination air release valve, PN 16, threaded ARI Type | Nr | 3
C5007 | 160mm x 2'' UPVC Saddle clamp, PN 16 | Nr | 3
C5008 | 3'' Hex Nipple | Nr | 3
C5009 | 3'' peglar gate valve. | Nr | 3
NON RETURN VALVES & WASH OUTS
C5010 | 6'' AVK Sluize valve | Nr | 4
C5011 | 4'' AVK Sluize valve | Nr | 1
C5012 | 6'' x 4'' x 6'' fabricated steel flanged Reducing Tee | Nr | 1
C5013 | 110mm UPV Loose flange, complete with bolts and nuts | Nr | 1
Chambers, ducts, culverts, crossings, thrust, anchor blocks, reinstatement and others pipework ancillaries
Valve Chambers- Internal Dimensions to fit as detailed on Drawing
Note:- Items for Work in this class shall include:- i. Excavation, preparation of surfaces, disposal of surplus excavated material, shoring sides of excavation, backfilling and removal of redundant services. ii. Concrete, Reinforcement, Formwork, Joints and Finishes. iii. Include for supply and fixing of removable precast concrete cover slab, mild steel frame, lifting / opening mechanism, step irons, compacted granular fill, rendering of exposed blockwork etc;. iv.Tips for disposal of excavated material or debris to be identified by the Contractor in liaison with the Local Authorities.
Air valve Chamber (1.5m x 1.2m)
C5014 | Depth n.e 1.5 m | Nr | 3
C5015 | Depth 1.5 - 2.0m | Nr | 0
Washout Chamber & Oftake (2m x 2.5m)
C5016 | Including concrete outfall works depth n.e 2.5 m | Nr | 4
Crossings
C5017 | DN 160mm Overcrossing on River Maraigushu | Nr | 1
C5018 | Allow for crossing existing drains and sewers, and reinstate these after construction of the water line has been completed. Pipe bore 100mm-300mm | Nr | 4
Micro-tunnelling below bituminous roads
Rates quoted shall be deemed to include for costs incurred on relevant roads authorities levies, traffic control, signage and safety measures during execution of the works and provision and installation of appropriate black pipe sleaves
C5019 | DN 160 - 300mm | m | 120
C5020 | Extra over microtunnelling in rock | m3 | 20
Reinstatement
Breaking up, temporary and permanent reinstatement of murram road (Width of road cutting n.e 2m) with 300mm thick well graded stabilised gravel with 3% cement content base compacted using a 8-10 tonne roller to the satisfaction of the Engineer . Nominal bore n.e. 300mm. Contractor to allow for liason with relevant local authorities and obtaining approval for completed works in his rates. Rate quoted shall be deemed to include UPVC waste water pipes class 41 for sleave works.
C5021 | OD 250 HDPE Pipe | m | 70
C5022 | OD 160mm HDPE Pipe | m | 240
Other Pipework Ancillaries
Supply and erect precast concrete marker post for the following:-
C5023 | Pipeline marker post | Nr | 19
C5024 | Air valve marker post | Nr | 1
C5025 | Washout marker post | Nr | 3
CLASS D: PIPEWORK - SUPPORTS AND PROTECTION, ANCILLARIES TO LAYING AND EXCAVATION
Extra to excavation and backfilling
D5001 | Extra Over excavation items for excavation in Soft rock | m3 | 120
D5002 | Ditto- but in Hard rock | m3 | 160
Beds
Selected Excavated granular material
D5003 | OD 250mm, depth n.e 150mm | m | 100
D5004 | OD 1600mm, depth n.e 150mm | m | 200
Sorrounds
Mass concrete Class 15/20
D5005 | DN 250 steel pipe | m | 24
D5006 | DN 160 steel pipe | m | 60
Concrete thrust blocks
Class 20/20 Mass Concrete
D5007 | For DN 250 45o bend volume 0.65 m3 | Nr | 3
D5008 | For DN 250 11.25o bend volume 0.15 m3 | Nr | 0
D5009 | For DN 250 30o bend volume 0.75 m3 | Nr | 0
D5010 | For DN 160 45o bend volume 0.95 m3 | Nr | 25
D5011 | For DN 160 90o bend volume 2.61 m3 | Nr | 15
Thrust blocks - RC, Volume 0.5 - 1.0m3
D5012 | For All junctions and branches | Nr | 6
Anchor blocks on Maraigushu River Crossing- RC, Volume n.e 0.1 m3
D5013 | Anchor blocks including metal strap and holddown bolts | Nr | 8
PAGE TOTAL CARRIED TO BILL COLLECTION PAGE
Note on F21: Evans Rwenji: Error in the original BoQ, Amount is 60,000 not 90,000
Note on F125: Evans Rwenji: Error in the original BoQ amount should be 28,500 not 45,000

## Bill No. 6-MIRERA DIST
BILL No. 6-MIRERA DISTRIBUTION
ITEM No. | DESCRIPTION | Unit | Quantity | Rate | Amount
CLASS A: GENERAL ITEM
Specified Requirements
Testing of Works
A6001 | Allow for hydrostatic pressure testing as specified for all the pipelines constructed under the contract to the satisfaction of the Engineer. | m | 26269
A6002 | Disinection of Pipelines: flushing with clear water, filling with water containing 0.05g/l calcium hyperchlorite, left for 24 hours. This includes supply of necessary equipment, materials, chemicals and water, measurement of residual chlorine, all as specified and safe disposal of disinfecting water to Engineer's approval. | m | 26269
Traffic Control and General Clearance
A6003 | Allow for temporary works for diversion of traffic during construction of pipelines across roads, including sign posting, liaison with Traffic Police Department, Local Authority construction of diversion roads etc. all to the satisfaction of the Engineer. Include provision for maintaining temporary vehicular access to individual plots at all times. | L.S | 1
A6004 | Allow for keeping trenches and other excavation free of waterwhich may have entered through ground seepage, rain or by other means as directed by the Engineer. | L.S | 1
A6005 | General clearance along the pipeline parth, width n.e 1.5m | ha | 3.9404
Cutting Trees
A6006 | Girth 0.5m - 1.0m | Nr | 4
A6007 | Girth 1.0m - 2.0m | Nr | 1
CLASS B: PIPEWORK - PIPES
Supply, transport to site and store Note: The following have been used to specify pipe diameters/types/classes. Pipe dimensions/working pressuresshall conform to KS150 -1452 - Part 2:2009.
High Density Polyethylene Pipes HDPE 100 SDR 17, ISO 4427:2007 with Butt Fusion (seamless) Jointing
B6001 | DN 160mm PN10 | m | 2034
B6002 | DN 140mm PN10 | m | 2059
B6003 | DN 125mm PN10 | m | 212
B6004 | DN 75mm PN 10 | m | 758
B6005 | DN 63mm PN 10 | m | 390
B6006 | DN 50mm PN 10 | m | 873
B6007 | DN 40mm PN 10 | m | 4528
B6008 | DN 32mm PN 10 | m | 9842
B6009 | DN 25mm PN 10 | m | 5573
| Transport from Site Store, Lay and Joint Pipes in Trench, include for Excavation, Preparation of Surfaces, Disposal of Excavated Material, Shoring Sides of Excavation Trenches, Backfilling and Final Reinstatement |  |  |  |  | #REF!
B6007 | DN 32 - 200mm in trenches depth 1.5m - 2.0m | m | 18388.3
B6008 | Ditto but depth 2.0 - 2.5m | m | 6567.25
B6009 | Ditto but depth 2.5 - 3.0m | m | 1313.45
| CLASS C: PIPEWORK - FITTINGS AND VALVES Rate to Include supply and installation, complete with all installation sundries such as gaskets, bolts, nut thread tapes etc and all anchoring works | [5 empty] | 31859
| Fittings | [5 empty] | 6324
C6001 | 160mmx 125mm HDPE Tee, PN 10 | Nr | 1
C6002 | Ditto but for 125mmx75mm | Nr | 2
C6003 | Ditto but for 125mm x 50mm | Nr | 2
C6004 | Ditto but for 125mmx 40mm | Nr | 1
C6005 | Ditto but for 125mm x 32mm | Nr | 1
C6006 | 160mm HDPE elbow 90 Deg | Nr | 4
C6007 | 125mm HDPE elbow 90 Deg | Nr | 2
C6008 | 75mm HDPE elbow 90 Deg | Nr | 2
C6009 | 40mm HDPE Compressed end Caps, PN 10 | Nr | 2
C6010 | 32mm HDPE Compressed end Caps, PN 10 | Nr | 9
C6011 | 25mm HDPE Compressed end Caps, PN 10 | Nr | 35
AIR VALVES & BULK METERS
C6012 | DN 4'' Woltman Bulk water meter, R 160 | Nr | 1
Washouts
C6013 | 110mm X 4'' UPVC Valve socket | Nr | 2
C6014 | 4'' Peglar Gate Valve | Nr | 2
C6015 | Ditto Butt 2'' | Nr | 2
C6016 | 4'' GI Tee | Nr | 1
C6017 | 4'' GI Nipple | Nr | 2
C6018 | 4'' x 2'' GI Reducing bush | Nr | 1
C6019 | 63mm HDPE Male adaptor | Nr | 1
PRV
C6020 | Pressure Reducing Valve DN150 | Nr | 1
Chambers, ducts, culverts, crossings, thrust, anchor blocks, reinstatement and others pipework ancillaries
Valve Chambers- Internal Dimensions to fit as detailed on Drawing
Note:- Items for Work in this class shall include:- i. Excavation, preparation of surfaces, disposal of surplus excavated material, shoring sides of excavation, backfilling and removal of redundant services. ii. Concrete, Reinforcement, Formwork, Joints and Finishes. iii. Include for supply and fixing of removable precast concrete cover slab, mild steel frame, lifting / opening mechanism, step irons, compacted granular fill, rendering of exposed blockwork etc;. iv.Tips for disposal of excavated material or debris to be identified by the Contractor in liaison with the Local Authorities.
Chamber (2.5m x 2m
C6021 | Depth n.e 2.5 m | Nr | 3
C6022 | Gate Valve Boxes (0.3m x 0.3m) | Nr | 125
Crossings
C6023 | Allow for crossing existing drains and sewers, and reinstate these after construction of the water line has been completed. Pipe bore 100mm-300mm | Nr | 5
Micro-tunneling below bituminous roads
Rates quoted shall be deemed to include for costs incurred on relevant roads authorities levies, traffic control, signage and safety measures during execution of the works and provision and installation of appropriate black pipe sleaves.
C6024 | DN 32 - 110mm (Road and Rail way) | m | 100
C6025 | Extra over microtunnelling in rock | m3 | 11
Reinstament
Breaking up, temporary and permanent reinstatement of murram road (Width of road cutting n.e 2m) with 300mm thick well graded stabilised gravel with 3% cement content base compacted using a 8-10 tonne roller to the satisfaction of the Engineer . Nominal bore n.e. 300mm. Contractor to allow for liason with relevant local authorities and obtaining approval for completed works in his rates. Rate quoted shall be deemed to include UPVC waste water pipes class 41 for sleave works.
C6026 | OD 32 - 110mm HDPE Pipe | m | 120
Other Pipework Ancillaries Supply and erect precast concrete marker post for the following
C6027 | Pipeline marker post | Nr | 50
C6028 | Wash out marker post | Nr | 1
CLASS D: PIPEWORK - SUPPORTS AND PROTECTION, ANCILLARIES TO LAYING AND EXCAVATION
Extra to excavation and backfilling
D6001 | Extra Over excavation items for excavation in Soft rock | m3 | 10
D6002 | -Ditto- but in Hard rock | m3 | 18
Concrete thrust blocks
Thrust blocks - RC, Volume 0.5 - 1.0m3
D6003 | For All junctions and branches | Nr | 6
PAGE TOTAL CARRIED TO BILL COLLECTION PAGE

## Bill No. 7-KINAMBA DIST
BILL No. 7-KINAMBA DISTRIBUTION
ITEM | DESCRIPTION | Unit | Quantity | Rate | Amount
CLASS A: GENERAL ITEM
Specified Requirements
Testing of Works
A7001 | Allow for hydrostatic pressure testing as specified for all the pipelines constructed under the contract to the satisfaction of the Engineer. | m | 36368
A7002 | Disinection of Pipelines: flushing with clear water, filling with water containing 0.05g/l calcium hyperchlorite, left for 24 hours. This includes supply of necessary equipment, materials, chemicals and water, measurement of residual chlorine, all as specified and safe disposal of disinfecting water to Engineer's approval. | m | 36368
Traffic Control and General Clearance
A7003 | Allow for temporary works for diversion of traffic during construction of pipelines across roads, including sign posting, liaison with Traffic Police Department, Local Authority construction of diversion roads etc. all to the satisfaction of the Engineer. Include provision for maintaining temporary vehicular access to individual plots at all times. | L.S | 1
A7004 | Allow for keeping trenches and other excavation free of waterwhich may have entered through ground seepage, rain or by other means as directed by the Engineer. | L.S | 1
A7005 | General clearance along the pipeline parth, width n.e 1.5m | ha | 5.4552
Cutting Trees
A7006 | Girth 0.5m - 1.0m | Nr | 5
A7007 | Girth 1.0m - 2.0m | Nr | 3
CLASS B: PIPEWORK - PIPES
Supply, transport to site and store Note: The following have been used to specify pipe diameters/types/ classes. Pipe dimensions/working pressuresshall conform to KS150 -1452 - Part 2:2009.
High Density Polyethylene Pipes HDPE 100 SDR 17, ISO 4427:2007 with Butt Fusion (seamless) Jointing
B7001 | DN 160mm PN12.5 | m | 1001
B7002 | DN 160mm PN10 | m | 2065
B7003 | DN 90mm PN 10 | m | 32
B7004 | DN 75mm PN 10 | m | 450
B7005 | DN 63mm PN 10 | m | 6830
B7006 | DN 50mm PN 10 | m | 2595
B7007 | DN 40mm PN 10 | m | 11380
B7008 | DN 32mm PN 10 | m | 11185
B7009 | DN 25mm PN 10 | m | 830
Transport from Site Store, Lay and Joint Pipes in Trench, include for Excavation, Preparation of Surfaces, Disposal of Excavated Material, Shoring Sides of Excavation Trenches, Backfilling and Final Reinstatement
B7010 | DN 25mm - 160mm in trenches depth 1.5m - 2.0m. | m | 27276
B7011 | Ditto but depth 2.0 - 2.5m | m | 9092
B7012 | Ditto but depth 2.5 - 3.0m | m | 0
CLASS J: PIPEWORK - FITTINGS AND VALVES Rate to Include supply and installation, complete with all installation sundries such as gaskets, bolts, nut thread tapes etc and all anchoring works
OFFTAKES
A. Tank Offtakes
J7001 | 200mm x 1.5'' fabricated steel saddle clamp | Nr | 1
J7002 | 1.5'' GI long Nipple | Nr | 1
J7003 | 1.5'' Weldon steel flange | Nr | 2
J7004 | Ditto but 1.5'' | Nr | 1
J7005 | 1.5'' Double flanged GI pipe, 0.5m long | Nr | 2
J7006 | 50mm HDPE stub end complete with flange | Nr | 1
Line offtake and line end fittings
J7008 | 160mm x 110mm x 75mm HDPE Tee, PN 10.5 | Nr | 1
J7009 | Ditto but for 160mmx 40mm | Nr | 1
J7010 | Ditto but for 160mm x 32mm | Nr | 2
J7011 | Ditto but for 63mm x 40mm | Nr | 4
J7012 | Ditto but for 63mm x 32mm | Nr | 5
J7013 | Ditto but for 40mm x 40mm | Nr | 8
J7014 | Ditto but for 40mm x 32mm | Nr | 7
J7015 | Ditto but for 40mm x 25mm | Nr | 4
J7016 | Ditto but for 32mm x 32mm | Nr | 6
J7017 | 160mm HDPE elbow 67.5 Deg | Nr | 1
J7018 | 63mm HDPE elbow 90 Deg | Nr | 1
J7019 | 63mm HDPE elbow 67.5 Deg | Nr | 1
J7020 | 40mm HDPE elbow 67.5 Deg | Nr | 2
J7021 | 40mm HDPE elbow 90 Deg | Nr | 9
J7022 | 32mm HDPE elbow 90 Deg | Nr | 16
J7023 | 40mm HDPE Compressed end Caps, PN 10 | Nr | 2
J7024 | 32mm HDPE Compressed end Caps, PN 10 | Nr | 18
J7025 | 25mm HDPE Compressed end Caps, PN 10 | Nr | 4
AIR VALVES & BULK METERS
J7027 | 1'' combination air release valve, PN 16, threaded ARI Type | Nr | 1
J7028 | 40mm x 1'' HDPE Saddle Clamp, PN 16 | Nr | 1
J7029 | 1'' Hex Nipple | Nr | 1
J7030 | 1'' peglar gate valve | Nr | 1
J7031 | DN 1.5'' Woltman Bulk water meter, R 160 | Nr | 1
Chambers, ducts, culverts, crossings, thrust, anchor blocks, reinstatement and others pipework ancillaries
Valve Chambers- Internal Dimensions to fit as detailed on Drawing
Note:- Items for Work in this class shall include:- i. Excavation, preparation of surfaces, disposal of surplus excavated material, shoring sides of excavation, backfilling and removal of redundant services. ii. Concrete, Reinforcement, Formwork, Joints and Finishes. iii. Include for supply and fixing of removable precast concrete cover slab, mild steel frame, lifting / opening mechanism, step irons, compacted granular fill, rendering of exposed blockwork etc;. iv.Tips for disposal of excavated material or debris to be identified by the Contractor in liaison with the Local Authorities.
Air valve Chamber (1.5m x 1.2m)
J7032 | Depth n.e 1.5 m | Nr | 1
Crossings
J7033 | Allow for crossing existing drains and sewers, and reinstate these after construction of the water line has been completed. Pipe bore 100mm-300mm | Nr | 8
Micro-tunneling below bituminous roads
Rates quoted shall be deemed to include for costs incurred on relevant roads authorities levies, traffic control, signage and safety measures during execution of the works and provision and installation of appropriate black pipe sleaves.
J7034 | DN 32 - 75mm | m | 100
J7035 | Extra over microtunnelling in rock | m3 | 8
Reinstament
Breaking up, temporary and permanent reinstatement of murram road (Width of road cutting n.e 2m) with 300mm thick well graded stabilised gravel with 3% cement content base compacted using a 8-10 tonne roller to the satisfaction of the Engineer . Nominal bore n.e. 300mm. Contractor to allow for liason with relevant local authorities and obtaining approval for completed works in his rates. Rate quoted shall be deemed to include UPVC waste water pipes class 41 for sleave works.
J7036 | OD 32 - 50mm HDPE Pipe | m | 80
Other Pipework Ancillaries Supply and erect precast concrete marker post for the following
J7037 | Pipeline marker post | Nr | 130
J7038 | Air valve marker post | Nr | 1
CLASS L: PIPEWORK - SUPPORTS AND PROTECTION, ANCILLARIES TO LAYING AND EXCAVATION
Extra to excavation and backfilling
L7001 | Extra Over excavation items for excavation in Soft rock | m3 | 10
L7002 | -Ditto- but in Hard rock | m3 | 18
Concrete thrust blocks
Thrust blocks - RC, Volume 0.5 - 1.0m3
L7003 | For All junctions and branches | Nr | 6
PAGE TOTAL CARRIED TO BILL COLLECTION PAGE

## Bill No. 8-KEROCHE BLOCK REHAB
BILL No. 8-KEROCHE BLOCK SYSTEM
ITEM | DESCRIPTION | Unit | Quantity | Rate | Amount
CLASS A: GENERAL ITEM
Specified Requirements
Testing of Works
A8001 | Allow for hydrostatic pressure testing as specified for all the pipelines constructed under the contract to the satisfaction of the Engineer. | m | 19770
A8002 | Disinection of Pipelines: flushing with clear water, filling with water containing 0.05g/l calcium hyperchlorite, left for 24 hours. This includes supply of necessary equipment, materials, chemicals and water, measurement of residual chlorine, all as specified and safe disposal of disinfecting water to Engineer's approval. | m | 19770
Traffic Control and General Clearance
A8003 | Allow for temporary works for diversion of traffic during construction of pipelines across roads, including sign posting, liaison with Traffic Police Department, Local Authority construction of diversion roads etc. all to the satisfaction of the Engineer. Include provision for maintaining temporary vehicular access to individual plots at all times. | L.S | 1
A8004 | Allow for keeping trenches and other excavation free of waterwhich may have entered through ground seepage, rain or by other means as directed by the Engineer. | L.S | 1
A8005 | General clearance along the pipeline parth, width n.e 1.5m | ha | 2.9655
Cutting Trees
A8006 | Girth 0.5m - 1.0m | Nr | 12
A8007 | Girth 1.0m - 2.0m | Nr | 2
CLASS B: PIPEWORK - PIPES
Supply, transport to site and store Note: The following have been used to specify pipe diameters/types/classes. Pipe dimensions/working pressuresshall conform to KS150 -1452 - Part 2:2009.
High Density Polyethylene Pipes HD-PE 100 SDR 17 , ISO 4427:2007 with Butt Fusion (seamless) Jointing
B8001 | DN 200mm PN10 | m | 302
B8002 | DN 160mm PN10 | m | 3370
B8003 | DN 63mm PN 10 | m | 5601
B8004 | DN 40mm PN 10 | m | 7406
B8005 | DN 32mm PN 10 | m | 1778
B8006 | DN 25mm PN 10 | m | 1615
Transport from Site Store, Lay and Joint Pipes in Trench, include for Excavation, Preparation of Surfaces, Disposal of Excavated Material, Shoring Sides of Excavation Trenches, Backfilling and Final Reinstatement
B8007 | DN 32 - 250mm in trenches depth 1.5m - 2.0m. | m | 13839
B8008 | Ditto but depth 2.0 - 2.5m | m | 4942.5
B8009 | Ditto but depth 2.5 - 3.0m | m | 988.5
CLASS C: PIPEWORK - FITTINGS AND VALVES Rate to Include supply and installation, complete with all installation sundries such as gaskets, bolts, nut thread tapes etc and all anchoring works
Fittings
C8001 | 180mmx63mm HDPE Tee, PN 10 | Nr | 1
C8002 | Ditto but for 160mmx63mm | Nr | 2
C8003 | Ditto but for 63mmx 63mm | Nr | 1
C8004 | Ditto but for 63mmx40mm | Nr | 3
C8005 | 32mm x 32mm x 25mm Y-Tee | Nr | 1
C8006 | 160mm HDPE elbow 112.5 Deg | Nr | 1
C8007 | 63mm HDPE elbow 90 Deg | Nr | 3
C8008 | 40mm HDPE elbow 90 Deg | Nr | 4
C8009 | Ditto but for 112.5 Deg | Nr | 2
C8010 | 50mm HDPE elbow 90 Deg | Nr | 2
C8011 | Ditto but 112.5 Deg | Nr | 2
C8012 | 32mm HDPE Compressed end Caps, PN 10 | Nr | 1
C8013 | 25mm HDPE Compressed end Caps, PN 10 | Nr | 9
AIR VALVES & BULK METERS
C8014 | DN 1.5'' Woltman Bulk water meter, R 160 | Nr | 1
Chambers, ducts, culverts, crossings, thrust, anchor blocks, reinstatement and others pipework ancillaries
Valve Chambers- Internal Dimensions to fit as detailed on Drawing
Note:- Items for Work in this class shall include:- i. Excavation, preparation of surfaces, disposal of surplus excavated material, shoring sides of excavation, backfilling and removal of redundant services. ii. Concrete, Reinforcement, Formwork, Joints and Finishes. iii. Include for supply and fixing of removable precast concrete cover slab, mild steel frame, lifting / opening mechanism, step irons, compacted granular fill, rendering of exposed blockwork etc;. iv.Tips for disposal of excavated material or debris to be identified by the Contractor in liaison with the Local Authorities.
Air valve Chamber (1.5m x 1.2m)
C8001 | Depth n.e 1.5 m | Nr | 1
Chamber (2.5m x 2m)
C8002 | Depth n.e 2.5 m | Nr | 3
C8003 | Gate Valve Boxes (0.3m x 0.3m) | Nr | 125
Crossings
C8004 | Allow for crossing existing drains and sewers, and reinstate these after construction of the water line has been completed. Pipe bore 100mm-300mm | Nr | 11
Micro-tunneling below bituminous roads
Rates quoted shall be deemed to include for costs incurred on relevant roads authorities levies, traffic control, signage and safety measures during execution of the works and provision and installation of appropriate black pipe sleaves.
C8005 | DN 25 - 180mm | m | 0
C8006 | Extra over microtunnelling in rock | m3 | 0
Reinstament
Breaking up, temporary and permanent reinstatement of murram road (Width of road cutting n.e 2m) with 300mm thick well graded stabilised gravel with 3% cement content base compacted using a 8-10 tonne roller to the satisfaction of the Engineer . Nominal bore n.e. 300mm. Contractor to allow for liason with relevant local authorities and obtaining approval for completed works in his rates. Rate quoted shall be deemed to include UPVC waste water pipes class 41 for sleave works.
C8007 | OD 25 - 180mm HDPE Pipe | m | 60
Other Pipework Ancillaries Supply and erect precast concrete marker post for the following:
C8008 | Pipeline marker post | Nr | 30
C8009 | Air valve marker post | Nr | 2
CLASS D: PIPEWORK - SUPPORTS AND PROTECTION, ANCILLARIES TO LAYING AND EXCAVATION
Extra to excavation and backfilling
D8001 | Extra Over excavation items for excavation in Soft rock | m3 | 16
D8002 | -Ditto- but in Hard rock | m3 | 8
Concrete thrust blocks
Thrust blocks - RC, Volume 0.5 - 1.0m3
D8003 | For All junctions and branches | Nr | 10
D8004 | Thread Tapes | Nr | 19
PAGE TOTAL CARRIED TO BILL COLLECTION PAGE